## Slide 1: HVAC SERVICES
Dr. Wameedh. T.M. Al-Tameemi

## Slide 2
Cooling Load Calculations
Air inside a building receives heat from a number of sources during the cooling season. If the temperature and humidity of the air are to be maintained at a comfortable level, this heat must be removed. The amount of heat that must be removed is called the cooling load.
The cooling load must be determined because it is the basis for selection of the proper size air conditioning equipment and distribution system. It is also used to analyze energy use and conservation.
يتلقى الهواء داخل المبنى الحرارة من عدد من المصادر خلال موسم التبريد. إذا كان يجب الحفاظ على درجة حرارة ورطوبة الهواء عند مستوى مريح ، فيجب إزالة هذه الحرارة. تسمى كمية الحرارة التي يجب إزالتها بحمل التبريد. يجب تحديد حمل التبريد لأنه الأساس لاختيار معدات تكييف الهواء ذات الحجم المناسب ونظام التوزيع. كما أنها تستخدم لتحليل استخدام الطاقة والحفاظ عليها.

## Slide 3
Cooling Load Calculations
COOLING LOAD CALCULATION PROCEDURES
In Heating Load calculations, we noted that the heat loss from a room at any instant was equal to the heating load at that time. With cooling, the situation is more complex. The amount of heat that must be removed (the cooling load) is not always equal to the amount of heat received at a given time.
This difference is a result of the heat storage and time lag effects. Of the total amount of heat entering the building at any instant, only a portion of it heats the room air immediately; the other part (the radiation) heats the building mass the roof, walls, floors, and furnishings. This is the heat storage effect. Only at a later time does the stored heat portion contribute to heating the room air. This is the time lag effect, as shown in Figure 1.

## Slide 4
Cooling Load Calculations
إجراءات حساب حمل التبريد
في حسابات حمل التدفئة ، لاحظنا أن فقدان الحرارة من الغرفة في أي لحظة كان مساويا لحمل التدفئة في ذلك الوقت. في حالة التبريد ، يكون الوضع أكثر تعقيدا. كمية الحرارة التي يجب إزالتها (حمل التبريد) لا تساوي دائما كمية الحرارة المكتسبة في وقت معين.
هذا الاختلاف هو نتيجة لتخزين الحرارة وتأثيرات التأخر الزمني. من إجمالي كمية الحرارة التي تدخل المبنى في أي لحظة ، يقوم جزء منها فقط بتسخين هواء الغرفة على الفور ؛ الجزء الآخر (الإشعاع) يسخن كتلة المبنى من السقف والجدران والأرضيات والمفروشات ويسمى تأثير تخزين الحرارة. تساهم كمية الحرارة المخزنة في تسخين هواء الغرفة في وقت لاحق . هذا هو تأثير الفارق الزمني ، كما هو موضح في الشكل 1.

## Slide 5
Cooling Load Calculations
The room cooling load: is the rate at which heat must be removed from the room air to
maintain it at the design temperature and humidity.
The thermal storage effect and resulting time lag cause the cooling load to often be different in value from the entering heat (called the instantaneous heat gain). An example is shown in Figure 2. Note that during the time of day at which the instantaneous heat gain is the highest (the afternoon), the cooling load is less than the instantaneous heat gain. This is because some of this heat is stored in the building mass and is not heating the room air. Later in the day, the stored heat plus some of the new entering heat is released to the room air, so the cooling load becomes greater than the instantaneous heat gain.

## Slide 6
Cooling Load Calculations
حمل تبريد الغرفة: هو المعدل الذي يجب فيه إزالة الحرارة من هواء الغرفة للحفاظ عليها في درجة حرارة التصميم والرطوبة.
يؤدي تأثير التخزين الحراري والتأخر الزمني الناتج عن ذلك إلى اختلاف حمل التبريد في كثير من الأحيان عن الحرارة الداخلة (تسمى كسب الحرارة الفوري). ويرد مثال على ذلك في الشكل 2. لاحظ أنه خلال الوقت من اليوم الذي يكون فيه كسب الحرارة الفوري هو الأعلى (بعد الظهر) ، يكون حمل التبريد أقل من اكتساب الحرارة الفوري. وذلك لأن بعض هذه الحرارة يتم تخزينها في كتلة المبنى ولا يتم تسخين هواء الغرفة. في وقت لاحق من اليوم ، يتم إطلاق الحرارة المخزنة بالإضافة إلى بعض الحرارة الداخلة الجديدة إلى هواء الغرفة ، وبالتالي يصبح حمل التبريد أكبر من اكتساب الحرارة الفوري.

## Slide 7
Cooling Load Calculations
There are a few different, acceptable procedures for calculating cooling loads that take into account the phenomena we have discussed. All of them are more accurate than past methods and are often required in state energy codes and standards. These methods often lead to use of smaller equipment and sometimes result in less energy use.
The cooling load calculation procedure that will be explained here is called the CLF/CLTD method. This procedure is relatively easy to understand and use. One of its valuable features is that in learning it, one may understand better the effects we have been discussing.
هناك عدد قليل من الطرق المقبولة لحساب أحمال التبريد التي تأخذ في الاعتبار الظواهر التي ناقشناها. كلها أكثر دقة من الطرق السابقة وغالبا ما تكون مطلوبة في قوانين ومعايير الطاقة. غالبا ما يؤدي استخدام هذه الطرق إلى استخدام معدات أصغر في تبريد الفضاء وتؤدي في بعض الأحيان إلى استخدام أقل للطاقة. يسمى إجراء حساب حمل التبريد الذي سيتم شرحه هنا طريقة CLF / CLTD . هذه الطريقة سهلة الفهم والاستخدام نسبيا. واحدة من ميزاتها القيمة هي أنه تعلم هذه الطريقة قد يؤدي الى فهم أفضل للتأثيرات التي كنا نناقشها.

## Slide 8
Cooling Load Calculations
ROOM HEAT GAINS
The heat gain components that contribute to the room cooling load consist of the following (Figure 3):
1. Conduction through exterior walls, roof, and glass
2. Conduction through interior partitions, ceilings,
and floors ( unconditioned)
3. Solar radiation (through glass and absorbed by walls)
4. Lighting
5. People
6. Equipment
7. Heat from infiltration of outside air through openings
8. Heat gain through the walls of ducts
9. Heat gain from the fan work
It is convenient to arrange these heat gains into two groups-those from external sources outside the room, and those internally generated. From the earlier description, it is seen that items 1 through 3 are external heat gains, and items 4 through 6 are internal heat gains. Infiltration can be considered as a separate class.
It is also convenient to arrange the heat gains into a different set of two groups: sensible and latent heat gains. Sensible heat gains result in increasing the air temperature; latent heat gains are due to addition of water vapor, thus increasing humidity.
23 to 26 C DBT & 50% RH

## Slide 9
Cooling Load Calculations
مصادر الكسب الحراري للغرفة
تتكون مكونات كسب الحرارة التي تساهم في حمل تبريد الغرفة مما يلي (الشكل 3): 1. التوصيل من خلال الجدران الخارجية والسقف والزجاج 2. التوصيل من خلال الأقسام الداخلية والأسقف والأرضيات (غير المكيفة) 3. الإشعاع الشمسي (من خلال الزجاج والممتص من قبل الجدران) 4. الإضاءة 5. الناس 6. المعدات 7. الحرارة الناتجة عن تسلل الهواء الخارجي من خلال الفتحات 8. اكتساب الحرارة من خلال جدران مجاري التبريد 9. الحرارة المكتسبة جراء عمل مراوح اجهزة التبريد
من الملائم ترتيب مصادر الكسب الحراري إلى مجموعتين - مصادر خارجية خارج الغرفة ، و مصادر داخلية. من الوصف السابق ، يتضح أن العناصر من 1 إلى 3 هي مكاسب حرارية خارجية ، والبنود من 4 إلى 6 هي مكاسب حرارية داخلية. يمكن اعتبار التسلل فئة منفصلة. في بعض الاحيان يتم ترتيب مكاسب الحرارة في مجموعة مختلفة من مجموعتين: مكاسب الحرارة المحسوسة والكامنة. مكاسب الحرارة المحسوسة تؤدي إلى زيادة درجة حرارة الهواء. ترجع مكاسب الحرارة الكامنة إلى إضافة بخار الماء ، وبالتالي زيادة الرطوبة.
23 to 26 C DBT & 50% RH

## Slide 10
Cooling Load Calculations
CONDUCTION THROUGH EXTERIOR STRUCTURE
The cooling loads caused by conduction heat gains through the exterior roof, walls, and glass are each found from the following equation:
Q=U . A. CLTDc c-1
where
Q = cooling load for roof, wall, or glass, w
U = overall heat transfer coefficient for roof, wall, or glass, w-m2-k
A = area of roof, wall, or glass, m2
CLTDc = corrected cooling load temperature difference, K or c
The cooling load temperature difference (CLTD) is not the actual temperature difference between the outdoor and indoor air. It is a modified value that accounts for the heat storage/time lag effects.
الفرق في درجة حرارة حمل التبريد CLTD) ) ليس هو الفرق الفعلي في درجة الحرارة بين الهواء الخارجي والداخلي وإنما هي قيمة معدلة تمثل تأثيرات تخزين الحرارة / التأخر الزمني.

## Slide 11
Cooling Load Calculations
CONDUCTION THROUGH INTERIOR STRUCTURE
The heat that flows from interior unconditioned spaces to the conditioned space through partitions, floors, and ceilings can be found from Equation h-2:
Q= U. A. TD
If the temperature of the unconditioned space is not known, an approximation often used is to assume that it is at 3 F less than the outdoor temperature. Spaces with heat sources, such as boiler rooms, may be at a much higher temperature.
SOLAR RADIATION THROUGH GLASS
Radiant energy from the sun passes through transparent materials such as glass and becomes a heat gain to the room. Its value varies with time, orientation, shading, and storage effect. The solar cooling load can be found from the following equation:
Q=SHGF . A . SC . CLF c-2
Q = solar radiation cooling load for glass. W
SHGF = maximum solar heat gain factor, w-m2
A = area of glass, m2
SC = shading coefficient
CLF = cooling load factor for glass
The maximum solar heat gain factor (SHGF) is the maximum solar heat gain through single
clear glass at a given month, orientation, and latitude.

## Slide 12
Cooling Load Calculations
LIGHTING
The equation for determining cooling load due to heat gain from lighting is
QLighting= W UF BF CLF c-3
where Qlighting , heating gain by lighting w, W is the light power measured (w).
UF, utilizing factor = 1 in residence, commercial stores and shops, = 0.5 in industrial workshops.
BF, ballast factor for fluorescent lamps= 1.2 for most common fluorescent fixtures
CLF = cooling-load factor, which is depends on the number of lights and the operation time.
PEOPLE
The heat gain from people is composed of two parts, sensible heat and the latent heat resulting from perspiration. Some of the sensible heat may be absorbed by the heat storage effect, but not the latent heat. The equations for cooling loads from sensible and latent heat gains from people are:
Qs= qs n CLF c-4
QL=qL n c-5
Qs, QL = sensible and latent heat gains (loads)
qs, qL = sensible and latent heat gains per person
n = number of people
CLF = cooling load factor for people, which is depends on the physical activities.

## Slide 13
Cooling Load Calculations
EQUIPMENT AND APPLIANCES
The heat gain from equipment may sometimes be found directly from the manufacturer or the nameplate data, with allowance for intermittent use. Some equipment produces both sensible and latent heat.
INFILTRATION
Infiltration of air through cracks around windows or doors results in both a sensible and latent heat gain to the rooms and can be calculated as discussed in heating load calculations by using eq. h-3 and eq. h-4.
Qs= 1.22 V TC
QL = 3010 V. (Wi – Wo)

## Slide 14
Cooling Load Calculations
المعدات والأجهزة
يمكن في بعض الأحيان العثور على كسب الحرارة من المعدات مباشرة من الشركة المصنعة أو بيانات لوحة الاسم ، مع السماح للاستخدام المتقطع. تنتج بعض المعدات حرارة محسوسة وكامنة.
التسلل
يؤدي تسلل الهواء من خلال الشقوق حول النوافذ أو الأبواب إلى اكتساب حرارة محسوسة وكامنة إلى الغرف ويمكن حسابها كما هو موضح في حسابات حمل التدفئة باستخدام eq. h-3 و eq. h-4.

## Slide 15
Cooling Load Calculations
ROOM COOLING LOAD
The room cooling load is the sum of each of the cooling load components (roof, walls, glass. solar, people, equipment, and infiltration) in the room.
The following abbreviations will be used for convenience.
TCL, SCL, LCL = component total, sensible, latent cooling loads
RTCL, RSCL, RLCL = room total, sensible, latent cooling loads
BTCL, BSCL, BLCL = building total, sensible, latent cooling loads
CTCL, SCSL, CLCL = coil total, sensible, latent cooling loads
COOLING COIL LOAD
After the building cooling load is determined, the cooling coil load is found.
The cooling coil load is the rate at which heat must be removed by the air conditioning
equipment cooling coil(s).
The cooling coil load will be greater than the building load because- there are heat gains to the air conditioning system itself. These gains may include:
I. Ventilation (outside air)
2. Heat gains to ducts
3. Heat produced by the air conditioning system fans and pumps
4. Air leakage from ducts

## Slide 16
Cooling Load Calculations
VENTILATION
Some outside air is generally brought 'into a building for health and comfort reasons. The sensible and latent heat of this air is usually greater than that of the room air, so it becomes part of the cooling load. The excess heat is usually removed in the cooling equipment, however, so it is part of the cooling coil load but not the building load.
HEAT GAIN TO DUCTS
The conditioned air flowing through ducts will gain heat from the surroundings. If the duct passes through conditioned spaces, the heat gain results in a useful cooling effect, but for the ducts passing through unconditioned spaces it is a loss of sensible heat that must be added to the BSCL. The heat gain can be calculated from the heat transfer Equation h-2.
Example: A 91cm. by 30cm. duct, 15m long, carrying air at 15.5c, runs through a space at 32c. The duct is insulated to an overall U = 0.25. What is the heat gain to the air in the duct?
Q = U A TD -----h2
A= surface area of the duct = (2*0.91+2*0.3)*15= 36.3 m2
Q= 0.25 * 36.3 *(32-15.5) = 149.74 W

## Slide 17
Cooling Load Calculations
Some designers find it reasonably accurate to add a percentage to the supply duct heat gain, rather than going through elaborate calculations. For insulated supply ducts, 1-3% of the building sensible load (BSCL) is suggested, depending on the extent of ductwork.
FAN AND PUMP HEAT
Some of the energy from the system fans and pumps is converted into heat through friction and other effects, and becomes part of the sensible heat gain that should be added to the load.

## Slide 18
Cooling Load Calculations
DUCT AIR LEAKAGE
Duct systems will leak air at joints. Unfortunately, many systems have unnecessarily high air leakage due to sloppy installation. However, a careful job should limit duct leakage to 5% or less of the total CFM. If ducts are outside the conditioned space, the effect of leakage must be added to the load. If the air leaks into the conditioned space, then it does useful cooling, but care should be taken that it is not distributed to the wrong location.
SUPPLY AIR CONDITIONS
After the sensible and latent heat gains are calculated, the required supply air conditions (flow rate, temperature, and humidity) necessary to satisfy room conditions are determined.
التسرب من مجاري الهواء
تقوم أنظمة مجاري الهواء في بعض الاحيان بتسريب الهواء عند المفاصل. العديد من انظمة مجاري الهواء تحتوي على تسرب هواء مرتفع دون داع بسبب التثبيت الغير جيد. ومع ذلك ، يجب أن يحد التثبيت الجيد من تسرب المجرى إلى 5٪ أو أقل من إجماليCFM . إذا كانت المجاري خارج المساحة المكيفة ، فيجب إضافة تأثير التسرب إلى حمل التبريد. إذا تسرب الهواء إلى المساحة المكيفة ، فإنه يقوم بتبريد مفيد ، ولكن يجب توخي الحذر من عدم توزيعه على الموقع الخطأ.
ظروف الهواء المجهز
بعد حساب مكاسب الحرارة المحسوسة والكامنة ، يتم تحديد ظروف الهواء المجهز المطلوبة (معدل التدفق ودرجة الحرارة والرطوبة) اللازمة لتلبية ظروف الغرفة.

## Slide 19
Cooling Load Calculations
Example CLF/CLTD

## Slide 20
Cooling Load Calculations
Roof construction
Conventional roof-attic-ceiling combination U = 0.28 W/(m2·K)
Wall construction
Brick, insulation, gypsum wallboard U = 0.34 W/(m2·K)
Partition wall U = 0. 4 W/(m2·K)
Doors
Wood, solid core U = 1.82 W/(m2·K)
Windows
U = 2.84 W/(m2·K)
SHGC = 0.67
SC=0.62
CLF=0.81
Outdoor design conditions
Temperature of 35°C dry bulb with a 13 K daily range
Relative humidity ratio of 0.0136 kg vapour/kg dry air (23.7 °C wet bulb)
Indoor design conditions
Temperature of 24 °C dry bulb
Relative humidity ratio of 50%
Occupancy
Four persons, qs= 67w per person, CLF= 0.8
ql=31w per person
Appliances and lights
470 W for the kitchen and 50% in the living room
CLTDc west = 14 part = 7 roof=27
Find the cooling load for living room?
Solution
Sensible Load
The cooling load must be made on a room-by-room basis to determine the proper distribution of air.
Sensible heat gains
For walls, roof and doors
Q=U A CLTDc
Wall- west wall
A=(6.1*2.4)-(0.9*2.1)-(1.8*2.4) = 8.43m2
Q= 0.34*8.43*14 = 40.1W

## Slide 21
Cooling Load Calculations
A=(7.3*2.4) = 17.52 m2
Q= 0.4 *17.52*7 = 49 W
Partition wall
Roof
A=(7.3*6.1) = 44.53 m2
Q= 0.28 *44.53*27 = 336.6 W
door
A=(0.9*2.1) = 1.89 m2
Q= 1.82 *1.89*14 = 48 W
Window,
Qcond=U*A*CLTD = 2.84*4.32*14=171.76w
A=(1.8*2.4) = 4.32 m2
Qsol= A*SHGC*SC*CLF = 4.32*0.67*0.62*0.81=1.45w

## Slide 22
Cooling Load Calculations
Occupancy
Q =qs*n*CLF= 67 *4 *0.8= 214W
Appliances (assuming that 50% of the kitchen load is picked up in the living room)
Q =470*0.5 = 235W
Infilteration
V = 14.85l/s
Q =1.22 V TD = 1.22*14.85*(35-24) = 217.4W
Latent Load
Occupancy
Q = ql*n= 31*4=124W
Infilteration
QL = 3010 V. (Wi – Wo) , V = 14.851, from chart Wi= 0.0093, Wo=0.0136
Ql= 3010*14.851*(0.0136-0.0093) = 192w
Qs total=TSCL = 49+336.6+48+171.76+1.45+214+235+217.4=1273.21W
Ql total = 124+192=316W
Room cooling load = 316+1273.21=1589.21w =1.589Kw = 1.589* 0.284345 =0.45 RT

## Slide 23
HVAC
Next lecture: HVAC Systems
Thank you very much
Reference: Air conditioning principles and systems
An energy approach Edward G. Pita
ASHRAE Handbook, fundamental 2021
Psychrometric calculator link:
https://www.kwangu.com/work/psychrometric.htm