## Slide 1: HVAC SERVICES
Dr. Wameedh. T.M. Al-Tameemi

## Slide 2
HVAC INTRODUCTION
Heating, Ventilating and Air Conditioning, HVAC, is a huge field. HVAC systems include a range from the simplest hand-stoked stove, used for comfort heating, to the extremely reliable total air-conditioning systems found in submarines and space shuttles. Cooling equipment varies from the small domestic unit to refrigeration machines that are 10,000 times the size, which are used in industrial processes. Depending on the complexity of the requirements, the HVAC designer must consider many more issues than simply keeping temperatures comfortable.
التدفئة , التهوية وتكييف الهواء، التكييف، هو حقل ضخم. وتشمل أنظمة التكييف مجموعة من أبسط موقد يدوي، يستخدم للتدفئة المريحة، إلى إجمالي أنظمة تكييف الهواء الموثوقة للغاية الموجودة في الغواصات ومكوكات الفضاء. معدات التبريد تختلف من وحدة محلية صغيرة الى آلات التبريد التي هي 10،000 أضعاف الحجم، والتي تستخدم في العمليات الصناعية. اعتمادا على المتطلبات المعقدة، يجب على مصمم التكييف النظر في العديد من القضايا أكثر من مجرد الحفاظ على درجات الحرارة مريحة.

## Slide 3
HVAC INTRODUCTION
People have used fire for heating. Initially, the air required to keep the fire going ensured adequate ventilation for the occupants. However, as central furnaces with piped steam or hot water became available for heating, the need for separate ventilation became apparent. By the late 1880s, rules of thumb for ventilation design were developed and used in many countries. In 1851 Dr. John Gorrie was granted U.S. patent 8080 for a refrigeration machine. By the 1880s, refrigeration became available for industrial purposes. Initially, the two main uses were freezing meat for transport and making ice. However, in the early 1900s there was a new initiative to keep buildings cool for comfort. Cooling the New York Stock Exchange, in 1902, was one of the first comfort cooling systems. Comfort cooling was called “air conditioning.” The term “air conditioning” has gradually changed, from meaning just cooling, to the total control of: (Temperature- Moisture in the air (humidity)-Supply of outside air for ventilation- Filtration of airborne particles- and Air movement in the occupied space.
استخدم الناس النار للتدفئة. يعتبرالهواء المطلوب للحفاظ على اتقاد النار اساسي لضمان التهوية الكافية لشاغلي المكان. ومع ذلك، وبالرغم من استخدام الأفران المركزية المحتوية على انابيب البخار أو الماء الساخن للتدفئة، أصبحت الحاجة واضحة إلى التهوية بشكل منفصل. وبحلول أواخر ثمانينيات القرن التاسع عشر، تم تطوير قواعد عامة لتصميم التهوية واستخدامها في العديد من البلدان. في عام 1851 منح الدكتور جون غوري براءة اختراع أمريكية 8080 لآلة تبريد. وبحلول ثمانينيات القرن التاسع عشر، أصبح التبريد متاحا للأغراض الصناعية. في البداية، كان الاستخدامان الرئيسيان تجميد اللحوم لنقلها وصنع الثلج. ومع ذلك ، في أوائل القرن العشرين ، كانت هناك مبادرة جديدة للحفاظ على المباني باردة للراحة. تبريد بورصة نيويورك، في عام 1902، كان واحدا من أول أنظمة التبريد الراحة. كان يطلق على التبريد المريح اسم "تكييف الهواء". مصطلح "تكييف الهواء" قد تغير تدريجيا، من معنى التبريد فقط، إلى السيطرة الكاملة على: (درجة الحرارة- الرطوبة في الهواء (الرطوبة)-تجهيز الهواء الخارجي للتهوية- ترشيح الجسيمات المحمولة جوا- وحركة الهواء في الفضاء المشغول.

## Slide 4
Introduction to Air-conditioning Processes
The term “air conditioning,” when properly used, now means the total control of temperature, moisture in the air (humidity), supply of outside air for ventilation, filtration of airborne particles, and air movement in the occupied space. There are seven main processes required to achieve full air conditioning and they are listed and explained below: The processes are:
1. Heating—the process of adding thermal energy (heat) to the conditioned space for the purposes of raising or maintaining the temperature of the space.
2. Cooling—the process of removing thermal energy (heat) from the conditioned space for the purposes of lowering or maintaining the temperature of the space.
3. Humidifying—the process of adding water vapor (moisture) to the air in the conditioned space for the purposes of raising or maintaining the moisture content of the air.
4. Dehumidifying—the process of removing water vapor (moisture) from the air in the conditioned space for the purposes of lowering or maintaining the moisture content of the air.
5. Cleaning—the process of removing particulates, (dust etc.,) and biological contaminants, (insects, pollen etc.,) from the air delivered to the conditioned space for the purposes of improving or maintaining the air quality.
6. Ventilating—the process of exchanging air between the outdoors and the conditioned space for the purposes of diluting the gaseous contaminants in the air and improving or maintaining air quality, composition and freshness. Ventilation can be achieved either through natural ventilation or mechanical ventilation. Natural ventilation is driven by natural draft, like when you open a window. Mechanical ventilation can be achieved by using fans to draw air in from outside or by fans that exhaust air from the space to outside.
7. Air Movement—the process of circulating and mixing air through conditioned spaces in the building for the purposes of achieving the proper ventilation and facilitating the thermal energy transfer.
The requirements and importance of the seven processes varies. In a climate that stays warm all year, heating may not be required at all. Conversely, in a cold climate the periods of heat in the summer may be so infrequent as to make cooling unnecessary. In a dry desert climate, dehumidification may be redundant, and in a hot, humid climate dehumidification may be the most important design aspect of the air-conditioning system.

## Slide 5
Introduction to Air-conditioning Processes
مصطلح "تكييف الهواء"، عند استخدامها بشكل صحيح، يعني الآن السيطرة الكاملة على درجة الحرارة، والرطوبة في الهواء (الرطوبة)، وتوريد الهواء الخارجي للتهوية، وترشيح الجسيمات المحمولة جوا، وحركة الهواء في الفضاء المحتل. هناك سبع عمليات رئيسية مطلوبة لتحقيق تكييف الهواء الكامل ويتم سردها وشرحها أدناه: العمليات هي:
1. التدفئة – عملية إضافة الطاقة الحرارية (الحرارة) إلى المساحة المكيفة لأغراض رفع أو الحفاظ على درجة حرارة الفضاء.
2. التبريد – عملية إزالة الطاقة الحرارية (الحرارة) من المساحة المكيفة لأغراض خفض أو الحفاظ على درجة حرارة الفضاء.
3. الترطيب – عملية إضافة بخار الماء (الرطوبة) إلى الهواء في الفضاء المكيف لأغراض رفع أو الحفاظ على محتوى الرطوبة في الهواء.
4. إزالة الرطوبة – عملية إزالة بخار الماء (الرطوبة) من الهواء في الفضاء المكيف لأغراض خفض أو الحفاظ على محتوى الرطوبة في الهواء.
5. التنظيف – عملية إزالة الجسيمات ، (الغبار وما إلى ذلك) والملوثات البيولوجية ، (الحشرات ، حبوب اللقاح وما إلى ذلك) من الهواء الذي يتم توصيله إلى الفضاء المكيف لأغراض تحسين جودة الهواء أو الحفاظ عليها.
6. التهوية – عملية تبادل الهواء بين الهواء الطلق والفضاء المكيف لأغراض تمييع الملوثات الغازية في الهواء وتحسين أو الحفاظ على جودة الهواء وتكوينه ونضارته. يمكن تحقيق التهوية إما عن طريق التهوية الطبيعية أو التهوية الميكانيكية. التهوية الطبيعية مدفوعة بمشروع طبيعي ، مثل عند فتح النافذة. يمكن تحقيق التهوية الميكانيكية باستخدام المراوح لرسم الهواء من الخارج أو من قبل المراوح التي تستنفد الهواء من الفضاء إلى الخارج.
7. حركة الهواء – عملية تدوير وخلط الهواء من خلال المساحات المكيفة في المبنى لأغراض تحقيق التهوية المناسبة وتسهيل نقل الطاقة الحرارية.
وتختلف متطلبات وأهمية العمليات السبع. في المناخ الذي يبقى دافئا طوال العام، قد لا تكون هناك حاجة إلى التدفئة على الإطلاق. وعلى العكس من ذلك، في المناخ البارد قد تكون فترات الحرارة في فصل الصيف نادرة جدا لجعل التبريد غير ضروري. وفي مناخ صحراوي جاف، قد تكون إزالة الرطوبة زائدة عن الحاجة، وفي مناخ حار ورطب، قد يكون إزالة الرطوبة أهم جانب من جوانب التصميم في نظام تكييف الهواء.

## Slide 6
Introducing the Psychrometric Chart
Many of the air-conditioning processes involve air that is experiencing energy changes. These changes arise from changes in the air’s temperature and its moisture content. The relationships between temperature, moisture content, and energy are most easily understood using a visual aid called the “psychrometric chart.”
The psychrometric chart is an industry-standard tool that is used to visualize the interrelationships between dry air, moisture and energy.
If you are responsible for the design or maintenance of any aspect of air conditioning in buildings, a clear and comfortable understanding of the chart will make your job easier. Initially, the chart can be intimidating, but as you work with it you will discover that the relationships that it illustrates are relatively easy to understand. Once you are comfortable with it, you will discover that it is a tool that can make it easier to troubleshoot air-conditioning problems in buildings.
The psychrometric chart is built upon two simple concepts.
1. Indoor air is a mixture of dry air and water vapor.
2. There is a specific amount of energy in the mixture at a specific temperature and pressure.
العديد من عمليات تكييف الهواء تنطوي على الهواء الذي يشهد تغييرات في الطاقة. تنشأ هذه التغيرات من التغيرات في درجة حرارة الهواء ومحتوى الرطوبة. فهم العلاقات بين درجة الحرارة، ومحتوى الرطوبة، والطاقة يكون اسهل باستخدام مخطط يسمى بالـ"المخطط المصردي". و هو أداة قياسية صناعية تستخدم لتصور العلاقات المتبادلة بين الهواء الجاف والرطوبة والطاقة.
إذا كنت مسؤولا عن تصميم أو صيانة أي جانب من جوانب تكييف الهواء في المباني، فإن فهمم المخطط سيجعل عملك أسهل. في البداية، يمكن أن يكون المخطط معقدا، ولكن أثناء العمل معه ستكتشف أن العلاقات التي يوضحها سهلة الفهم نسبيا. بمجرد أن تتمرس بالعمل مع المخطط، ستكتشف أنها أداة يمكن أن تسهل استكشاف مشكلات تكييف الهواء في المباني.
تم بناء الرسم البياني النفسي على مفهومين بسيطين.
1. الهواء الداخلي هو خليط من الهواء الجاف وبخار الماء.
2. هناك كمية محددة من الطاقة في الخليط في درجة حرارة وضغط محددة.

## Slide 7
Introducing the Psychrometric Chart
Indoor air is a mixture of dry air and water vapor.
The air we live in is a mixture of both dry air and water vapor. Both are invisible gases. The water vapor in air is also called moisture or humidity. The quantity of water vapor in air is expressed as “g of water vapor per kg of air.” This ratio is called the “humidity ratio,” abbreviation W and the units are g of water/kg of dry air, gw/kgda, often abbreviated to g/kg. The exact properties of moist air vary with pressure. Because pressure reduces as altitude increases, the properties of moist air change with altitude. Typically, psychrometric charts are printed based on standard pressure at sea level. For the rest of this course we will consider pressure as constant.
To understand the relationship between water vapor, air and temperature, we will consider two conditions:
First Condition: The temperature is constant, but the quantity of water vapor is increasing. If the temperature remains constant, then, as the quantity of water vapor in the air increases, the humidity increases. However, at every temperature point, there is a maximum amount of water vapor that can co-exist with the air.
The point at which this maximum is reached is called the saturation point. If more water vapor is added after the saturation point is reached, then an equal amount of water vapor condenses, and takes the form of either water droplets or ice crystals.
Outdoors, we see water droplets in the air as fog, clouds or rain and we see ice crystals in the air as snow or hail. The psychrometric chart only considers the conditions up to the saturation point; therefore, it only considers the effects of water in the vapor phase, and does not deal with water droplets or ice crystals.
Second Condition: The temperature is dropping, but the quantity of water vapor is constant. If the air is cooled sufficiently, it reaches the saturation line. If it is cooled even more, moisture will condense out and dew forms. For example, if a cold canned drink is taken out of the refrigerator and left for a few minutes, the container gets damp. This is because the moist air is in contact with the chilled container. The container cools the air that it contacts to a temperature that is below saturation, and dew forms. This temperature, at which the air starts to produce condensation, is called the dew point temperature.

## Slide 8
Introducing the Psychrometric Chart
Indoor air is a mixture of dry air and water vapor.
الهواء الذي نعيش فيه هو مزيج من الهواء الجاف وبخار الماء. كلاهما غازات غير مرئية. ويسمى بخار الماء في الهواء أيضا بالرطوبة. يتم التعبير عن كمية بخار الماء في الهواء على أنها «غرام من بخار الماء لكل كيلوغرام من الهواء". وتسمى هذه النسبة بـ «الرطوبة النسبية W "، والوحدات هي غرام من الماء / كغم من الهواء الجاف، gw/kgda، وغالبا ما يختصر إلى غم / كغم. تختلف الخصائص الدقيقة للهواء الرطب مع الضغط. نظرا لتغير الضغط مع زيادة الارتفاع عن سطح البحر ، تتغير خصائص الهواء الرطب مع الارتفاع. عادة، تتم طباعة المخططات المصردية على أساس الضغط القياسي على مستوى سطح البحر. لبقية هذا الفصل الدراسي, سوف نعتبر الضغط ثابتا.
لفهم العلاقة بين بخار الماء والهواء ودرجة الحرارة ، سنفترض حالتين:
الحالة الأولى: درجة الحرارة ثابتة ، ولكن كمية بخار الماء آخذة في الازدياد. إذا كانت درجة الحرارة ثابتة، فان الرطوبة النسبية تزداد بارتفاع كمية بخار الماء في الهواء. ومع ذلك، فانه لكل درجة حرارة، هناك كمية قصوى من بخار الماء التي يمكن أن تتعايش مع الهواء. وتسمى النقطة التي يتم فيها الوصول إلى هذا الحد الأقصى نقطة التشبع. إذا تمت إضافة المزيد من بخار الماء بعد الوصول إلى نقطة التشبع ، فإن كمية متساوية من بخار الماء تتكثف ، وتتخذ شكل قطرات الماء أو بلورات الثلج.
في الهواء الطلق، نرى قطرات الماء في الهواء كضباب أو سحب أو مطر ونرى بلورات الجليد في الهواء كثلج أو برد. لا يأخذ المخطط في الاعتبار الظروف الخارجة عن نقطة التشبع؛ لذلك ، فإنه لا ينظر إلا في آثار الماء في مرحلة البخار ، ولا يتعامل مع قطرات الماء أو بلورات الثلج.
الحالة الثانية: تنخفض درجة الحرارة ، ولكن كمية بخار الماء ثابتة. إذا تم تبريد الهواء بما فيه الكفاية، فإنه يصل إلى خط التشبع. إذا تم تبريده أكثر من ذلك ، فإن الرطوبة سوف تتكثف ويتكون الندى. على سبيل المثال، إذا تم إخراج مشروب بارد معلب من الثلاجة وترك لبضع دقائق، تصبح العلبة رطبة. وذلك لأن الهواء الرطب هو في اتصال مع الحاوية المبردة. تقوم الحاوية بتبريد الهواء الذي تتصل به إلى درجة حرارة أقل من التشبع ، ويتشكل الندى. وتسمى درجة الحرارة هذه، التي يبدأ فيها الهواء في إنتاج التكثيف، درجة حرارة نقطة الندى.

## Slide 9
Introducing the Psychrometric Chart
Indoor air is a mixture of dry air and water vapor.
Relative Humidity
Figure 1 is a plot of the maximum quantity of water vapor per kg of air against air temperature. The X-axis is temperature. The Y-axis is the proportion of water vapor to dry air, measured in pounds of water vapor per pound of dry air. The curved “maximum water vapor line” is called the “saturation line.” It is also known as 100% relative humidity, abbreviated to 100% rh.
At any point on the saturation line, the air has 100% of the water vapor per pound of air that can coexist with dry air at that temperature. When the same volume of air contains only half the weight of water vapor that it has the capacity to hold at that temperature, we call it 50% relative humidity or 50% rh. This is shown in Figure 2 Air at any point on the 50% rh line has half the water vapor that the same volume of air could have at that temperature.
As you can see on the chart, the maximum amount of water vapor that moist air can contain increases rapidly with increasing temperature. For example, moist air at the freezing point, 0 C, can contain only 0.4% of its weight as water vapor. However, indoors, at a temperature of 22 C the moist air can contain nearly 1.7% of its weight as water vapor—over four times as much.

## Slide 10
Introducing the Psychrometric Chart
Indoor air is a mixture of dry air and water vapor.
الرطوبة النسبية
يوضح الشكل 1 أقصى كمية من بخار الماء لكل كغم من الهواء مقابل درجة حرارة الهواء. المحور X هو درجة الحرارة. محور Y هو نسبة بخار الماء إلى الهواء الجاف ، تقاس بغرام من بخار الماء لكل كغم من الهواء الجاف. يسمى "خط بخار الماء الأقصى" المنحني "خط التشبع". يعرف أيضا ب الرطوبة النسبية 100%.
في أي نقطة على خط التشبع ، يحتوي الهواء على 100٪ من بخار الماء لكل كغم من الهواء الذي يمكن أن يتعايش مع الهواء الجاف في درجة الحرارة تلك. عندما يحتوي نفس حجم الهواء على نصف وزن بخار الماء فقط الذي لديه القدرة على الاحتفاظ به عند درجة الحرارة تلك ، نسميه رطوبة نسبية بنسبة 50٪ . يظهر هذا في الشكل 2 الهواء في أي نقطة على خط 50٪ لديه نصف بخار الماء الذي نفس حجم الهواء يمكن أن يكون في تلك درجة الحرارة.
كما ترون على الرسم البياني، فإن الحد الأقصى لكمية بخار الماء التي يمكن أن يحتوي عليها الهواء الرطب يزيد بسرعة مع ارتفاع درجة الحرارة. على سبيل المثال، الهواء الرطب عند نقطة التجمد، 0 C، يمكن أن تحتوي على 0.4٪ فقط من وزنه مبخر الماء. ومع ذلك، في الداخل، عند درجة حرارة 22 C يمكن أن يحتوي الهواء الرطب على ما يقرب من 1.7٪ من وزنه كبخار الماء - أكثر من أربعة أضعاف ذلك.

## Slide 11
Introducing the Psychrometric Chart
Indoor air is a mixture of dry air and water vapor.
Consider Figure 2-3, and this example:
On a miserable wet day it might be 5 C outside, with the air rather humid, at 80% relative humidity. Bring that air into your building. Heat it to 22 C. This brings the relative humidity down to about 25%. This change in relative humidity is shown in Figure 2-3, from Point 1→2. A cool damp day outside provides air for a dry day indoors! Note that the absolute amount of water vapor in the air has remained the same, at 4 grams of water vapor per kilogram of dry air; but as the temperature rises, the relative humidity falls.

## Slide 12
Introducing the Psychrometric Chart
Indoor air is a mixture of dry air and water vapor.
في الشكل 3، وهذا المثال: في يوم رطب عند درجة حرارة 5 مئوية، 80% رطوبة نسبية. عند احضار هذا الهواء إلى المبنى و تسخينه إلى 22 درجة مئوية فان هذا يرفع الرطوبة النسبية إلى حوالي 25٪. ويظهر هذا التغير في الرطوبة النسبية في الشكل 3، من النقطة 1→2. يوم رطب بارد في الخارج يوفر الهواء ليوم جاف في الداخل! لاحظ أن الكمية المطلقة لبخار الماء في الهواء ظلت كما هي، عند 4 غرامات من بخار الماء لكل كيلوغرام من الهواء الجاف؛ ولكن مع ارتفاع درجة الحرارة ، تنخفض الرطوبة النسبية.

## Slide 13
Introducing the Psychrometric Chart
There is a specific amount of energy in the air mixture at a specific temperature and pressure.
There is a specific amount of energy in the air water-vapor mixture at a specific temperature. The energy of this mixture is dependent on two measures:
1. The temperature of the air.
2. The proportion of water vapor in the air.
There is more energy in air at higher temperatures. The addition of heat to raise the temperature is called adding “sensible heat.” There is also more energy when there is more water vapor in the air. The energy that the water
vapor contains is referred to as its “latent heat.”
The measure of the total energy of both the sensible heat in the air and the latent heat in the water vapor is commonly called “enthalpy.” Enthalpy can be raised by adding energy to the mixture of dry air and water vapor. This can be accomplished by adding either or both
Sensible heat to the air
More water vapor, which increases the latent heat
of the mixture
On the psychrometric chart, lines of constant enthalpy slope down from left to right as shown in Figure 4 and are labeled “Enthalpy.”
The zero is arbitrarily chosen as zero at 0 C and zero moisture content. The unit measure for enthalpy is kilojoules per kilogram of dry air, abbreviated as kJ/kg.

## Slide 14
Introducing the Psychrometric Chart
There is a specific amount of energy in the air mixture at a specific temperature and pressure.
هناك كمية محددة من الطاقة في خليط الهواء وبخار الماء في درجة حرارة محددة. تعتمد طاقة هذا الخليط على مقياسين:
1. درجة حرارة الهواء. 2. نسبة بخار الماء في الهواء.
هناك المزيد من الطاقة في الهواء في درجات حرارة أعلى. وتسمى إضافة الحرارة لرفع درجة الحرارة إضافة "حرارة محسوسة". وهناك أيضا المزيد من الطاقة عندما يكون هناك المزيد من بخار الماء في الهواء. ويشار إلى الطاقة التي يحتوي عليها بخار الماء باسم "حرارته الكامنة".
مقياس الطاقة الإجمالية لكل من الحرارة المحسوسة في الهواء والحرارة الكامنة في بخار الماء يسمى عادة "enthalpy". يمكن زيادة Enthalpy عن طريق إضافة الطاقة إلى خليط الهواء الجاف وبخار الماء. ويمكن تحقيق ذلك عن طريق إضافة إما أو كل من الحرارة المحسوسة إلى الهواء المزيد من بخار الماء، مما يزيد من الحرارة الكامنة للخليط
على المخطط المصردي، خطوط المنحدر enthalpy مثبتة إلى أسفل من اليسار إلى اليمين كما هو مبين في الشكل 4 وتوصف بأنها "Enthalpy". يتم اختيار الصفر بشكل تعسفي كصفر في 0 C ومحتوى رطوبة صفر. مقياس الوحدة للإنثالبي هو كيلوجول لكل كيلوغرام من الهواء الجاف.

## Slide 15
Introducing the Psychrometric Chart
There is a specific amount of energy in the air mixture at a specific temperature and pressure.
Heating
The process of heating involves the addition of sensible heat energy. Figure 5 illustrates outside air at 5 C and almost 80% relative humidity that has been heated to 22 C. This process increases the enthalpy in the air from pproximately
16 kJ/kg to 33 kJ/kg. Note that the process line is horizontal because no water vapor is being added to or removed from the air—we are just heating the mixture. In the process, the relative humidity drops from almost 80% rh down to about 25% rh. Here is an example for you to try. Plot this process on Figure 6.Suppose it is a cool day with an outside temperature of 6 C and 50% rh. We have an air-conditioned space and the air is heated to 20 C. There is no change in the amount of water vapor in the air. The enthalpy rises from about 16 kJ/kg to 33 kJ/kg, an increase of 17 kJ/kg. As you can see, the humidity would have dropped to 20% rh. This is quite dry so let us assume that we are to raise the humidity to a more comfortable 50%. As you can see on the chart, this raises the enthalpy by an additional
11 kJ/kg.

## Slide 16
Introducing the Psychrometric Chart
There is a specific amount of energy in the air mixture at a specific temperature and pressure.
Heating
عملية التدفئة ينطوي على إضافة الطاقة الحرارية المحسوسة. يوضح الشكل 5 الهواء الخارجي عند 5 C والرطوبة النسبية بنسبة 80٪ تقريبا التي تم تسخينها إلى 22 درجة مئوية. هذه العملية يزيد من enthalpy في الهواء من حوالي 16 كيلوجول / كغ إلى 33 كيلوجول / كغ. لاحظ أن خط المعالجة أفقي لأنه لا يتم إضافة بخار الماء إلى الهواء أو إزالته منه - نحن نقوم بتسخين الخليط فقط. في هذه العملية، تنخفض الرطوبة النسبية من ما يقرب من 80٪ وصولا الى حوالي 25٪ .
هنا مثال لك للمحاولة. ارسم هذه العملية على الشكل 6. في يوم بارد مع درجة حرارة خارجية 6C و 50٪رطوبة نسبية. لدينا مساحة مكيفة الهواء ويتم تسخين الهواء إلى 20 درجة مئوية. لا يوجد أي تغيير في كمية بخار الماء في الهواء. يرتفع الenthalpy من حوالي 16 كيلوجول/كجم إلى 33 كيلوجول/كجم، بزيادة قدرها 17 كيلوجول/كجم. كما ترون، فإن الرطوبة قد انخفضت إلى 20٪ rh. هذا جاف جدا لذلك دعونا نفترض أننا رفعنا الرطوبة إلى 50٪ لتكون أكثر راحة. كما ترون على الرسم البياني في الشكل 7، وهذا يرفع enthalpy من قبل 11 كيلوجول / كغم إضافية.

## Slide 17
Introducing the Psychrometric Chart
There is a specific amount of energy in the air mixture at a specific temperature and pressure.
Humidification
The addition of water vapor to air is a process called “humidification.” Humidification occurs when water absorbs energy, evaporates into water vapor, and mixes with air. The energy that the water absorbs is called “latent heat.”
There are two ways for humidification to occur. In both methods, energy is added to the water to create water vapor.
1. Water can be heated. When heat energy is added to the water, the water is transformed to its gaseous state, steam that mixes into the air. In Figure 6, the vertical line, from Point 1 to Point 2, shows this process. The heat energy, 11 kJ/kg, is put into the water to generate steam (vaporize it), which is then mixed with the air.
In practical steam humidifiers, the added steam is hotter than the air and the piping loses some heat into the air. Therefore, the air is both humidified and heated due to the addition of the water vapor. This combined humidification and heating is shown by the dotted line which slopes a little to the right in Figure 6.
2. Water can evaporate by spraying a fine mist of water droplets into the air. The fine water droplets absorb heat from the air as they evaporate. Alternatively, but using the same evaporation process, air can be passed over a wet fabric, or wet surface, enabling the water to evaporate into the air.
In an evaporative humidifier, the evaporating water absorbs heat from the air to provide its latent heat for evaporation. As a result, the air temperature drops as it is humidified. The process occurs with no external addition or removal of heat. It is called an adiabatic process. Since there is no change in the heat energy (enthalpy) in the air stream, the addition of moisture, by evaporation, occurs along a line of constant enthalpy.

## Slide 18
Introducing the Psychrometric Chart
There is a specific amount of energy in the air mixture at a specific temperature and pressure.
Humidification
إضافة بخار الماء إلى الهواء هي عملية تسمى "الترطيب". يحدث الترطيب عندما يمتص الماء الطاقة، ويتبخر على شكل بخار الماء، ويخلط مع الهواء. الطاقة التي يمتصها الماء تسمى "الحرارة الكامنة". هناك طريقتان للترطيب و في كلتا الطريقتين، يتم إضافة الطاقة إلى الماء لتكوين بخار الماء.
1. يمكن تسخين المياه. عندما يتم إضافة الطاقة الحرارية إلى الماء، يتم تحويل المياه إلى حالته الغازية، البخار الذي يختلط في الهواء. في الشكل 6، يظهر الخط العمودي، من النقطة 1 إلى النقطة 2، هذه العملية. يتم وضع الطاقة الحرارية ، 11 كيلوجول / كجم ، في الماء لتوليد البخار (تبخيره) ، والذي يتم خلطه بعد ذلك مع الهواء. في مرطبات البخار العملية ، يكون البخار المضاف أكثر سخونة من الهواء وتفقد الأنابيب بعض الحرارة في الهواء. لذلك ، يتم ترطيب الهواء وتسخينه بسبب إضافة بخار الماء. يظهر هذا الترطيب والتدفئة المدمجين بواسطة الخط المنقط الذي ينحدر قليلا إلى اليمين في الشكل 6.
2. يمكن أن تتبخر المياه عن طريق رش رذاذ ناعم من قطرات الماء في الهواء. تمتص قطرات الماء الناعمة الحرارة من الهواء أثناء تبخرها. بدلا من ذلك، ولكن باستخدام نفس عملية التبخر، يمكن تمرير الهواء فوق نسيج رطب، أو سطح رطب، مما يمكن الماء من التبخر في الهواء.
في مرطب التبخر ، يمتص الماء المتبخر الحرارة من الهواء لتوفير حرارة كامنة للتبخر. ونتيجة لذلك، تنخفض درجة حرارة الهواء عند رطوبته. تحدث العملية بدون إضافة خارجية أو إزالة للحرارة. وتسمى عملية. adiabatic نظرا لإضافة الرطوبة ، عن طريق التبخر ، دون تسخين فان العملية تحدث على خط ثابت للانثالبي.

## Slide 19
Introducing the Psychrometric Chart
There is a specific amount of energy in the air mixture at a specific temperature and pressure.
Figure 7 shows the process. From Point 1, the moisture evaporates into the air and the temperature falls to 9 C, Point 2. During this evaporation, the relative humidity rises to about 95%. To reach our target of 20 C and 50% rh
we must now heat the moistened air at Point 2 from 9 C to 20C, Point 3, requiring 11 kJ/kg of dry air.
To summarize, we can humidify by adding heat to water to produce steam and mixing the steam with the air, or we can evaporate the moisture and heat the moistened air. We achieve the same result with the same input of heat by two different methods.
The process of evaporative cooling can be used very effectively in a hot, dry desert climate to pre-cool the incoming ventilation air. For example, outside air at 35 C and 15% relative humidity could be cooled to 26 C by passing it through an evaporative cooler. The relative humidity will rise, but only to about 40%. Even with no mechanical refrigeration, this results in a pleasant reduction in air temperature without raising the relative humidity excessively.

## Slide 20
Introducing the Psychrometric Chart
There is a specific amount of energy in the air mixture at a specific temperature and pressure.
ويبين الشكل 7 العملية. من النقطة 1، تتبخر الرطوبة في الهواء وتنخفض درجة الحرارة إلى 9 C، النقطة 2. خلال هذا التبخر ، ترتفع الرطوبة النسبية إلى حوالي 95٪. للوصول إلى هدفنا من 20 C و 50٪ rh يجب علينا الآن تسخين الهواء الرطب في النقطة 2 من 9 C إلى 20C، النقطة 3، التي تتطلب 11 كيلوجول / كجم من الهواء الجاف.
خلاصة لذلك، يمكننا ترطيب الهواء بإضافة الحرارة إلى الماء لإنتاج البخار وخلط البخار مع الهواء، أو أننا يمكن أن نبخر الرطوبة وتسخين الهواء الرطب. نحقق نفس النتيجة مع نفس مدخلات الحرارة من طريقتين مختلفتين. يمكن استخدام عملية التبريد التبخري بفعالية كبيرة في مناخ صحراوي حار وجاف لتبريد هواء التهوية الوارد مسبقا. على سبيل المثال، يمكن تبريد الهواء الخارجي عند 35 درجة مئوية والرطوبة النسبية بنسبة 15٪ إلى 26 درجة مئوية عن طريق تمريره عبر مبرد تبخري. الرطوبة النسبية سترتفع، ولكن فقط إلى حوالي 40٪. حتى مع عدم وجود التبريد الميكانيكية، وهذا يؤدي إلى انخفاض لطيف في درجة حرارة الهواء دون رفع الرطوبة النسبية بشكل مفرط.

## Slide 21
Introducing the Psychrometric Chart
Cooling and dehumidification
Cooling is most often achieved in an air-conditioning system by passing the moist air over a cooling coil. As illustrated in Figure 8, a coil is constructed of a long serpentine pipe through which a cold liquid or gas flows. This cold fluid is either chilled water, typically between 45 C and 75 C, or a refrigerant. The pipe is lined with fins to increase the heat transfer from the air to the cold fluid in the pipe. Figure 8 shows the face of the coil, in the direction of airflow. Depending on the coil design, required temperature drop, and moisture removal performance, the coil may have 2 to 8 rows of piping. Generally the more rows, the higher the moisture removal ability of the coil.
There are two results. First, the cooling coil cools the air as the air passes over the coils. Second, because the cooling fluid in the coil is usually well below the saturation temperature of the air, moisture condenses on the coil, and drips off, to drain away. This process reduces the enthalpy, or heat, of the air mixture and increases the enthalpy of the chilled water or refrigerant. In another part of the system, this added heat must be removed from the chilled water or refrigerant to recool it for reuse in the cooling coil.
The amount of moisture that is removed depends on several factors including:
• The temperature of the cooling fluid
• The depth of the coil
• Whether the fins are flat or embossed
• The air velocity across the coil.
An example of the typical process is shown in Figure 9.

## Slide 22
Introducing the Psychrometric Chart
التبريد والتجفيف
يتم تحقيق التبريد في معظم الأحيان في نظام تكييف الهواء عن طريق تمرير الهواء الرطب على ملفات التبريد. كما هو موضح في الشكل 8، يتم بناء لفائف من أنبوب ملتوي طويل يتدفق من خلاله سائل بارد أو غاز. هذا السائل البارد هو إما الماء المبرد، وعادة ما بين 4.5 C و 7.5 C، أو غاز تبريد. وتكون الأنابيب مع زعانف لزيادة نقل الحرارة من الهواء إلى السائل البارد في الأنابيب. الشكل 8 يظهر وجه الملف، في اتجاه تدفق الهواء. اعتمادا على تصميم الملف، انخفاض درجة الحرارة المطلوبة، وأداء إزالة الرطوبة، قد يحتوي الملف 2-8 صفوف من الأنابيب. عموما كلما ازداد عدد الصفوف، ترتفع قدرة إزالة الرطوبة من الملف.
هناك نتيجتان. أولا، يبرد ملف التبريد الهواء أثناء مرور الهواء خلال الملف. ثانيا، لأن سائل التبريد في الملف عادة ما يكون أقل بكثير من درجة حرارة التشبع في الهواء، تتكثف الرطوبة على الملف، وتقطر، لتصرف بعيدا. هذه العملية يقلل من الانثالبي، أو الحرارة، من خليط الهواء ويزيد من انثالبي الماء المبرد أو غاز التبريد. في جزء آخر من النظام، يجب إزالة هذه الحرارة المضافة من الماء المبرد أو المبرد لإعادة تبريده لإعادة استخدامه في لفائف التبريد.
تعتمد كمية الرطوبة التي تتم إزالتها على عدة عوامل منها:
• درجة حرارة سائل التبريد
• عمق الملفات
• ما إذا كانت الزعانف مسطحة أو منقوشة
• سرعة الهواء عبر الملف
. يظهر مثال العملية النموذجية في الشكل 9.

## Slide 23
Introducing the Psychrometric Chart
The warm moist air comes into the building at 25 C and 60% rh, and passes through a cooling coil. In this process, the air is being cooled to 13 C. As the moisture condenses on the coil, it releases its latent heat and this heat has to be removed by the cooling fluid. In Figure 2-9 the moisture removal enthalpy, A→B, is about a third of the enthalpy required to cool the air, B→C.This has been a very brief introduction to the concepts of the psychrometric chart.
A typical chart is shown in Figure 10. It looks complicated, but you know the simple underlying ideas:
* Indoor air is a mixture of dry air and water vapor.
* There is a specific amount of total energy, called enthalpy, in the mixture at a specific temperature, moisture content, and pressure.
* There is a maximum limit to the amount of water vapor in the mixture at any particular temperature.

## Slide 24
Introducing the Psychrometric Chart
يأتي الهواء الرطب الدافئ إلى المبنى بمعدل 25 درجة مئوية و60٪ من ال rh، ويمر عبر لفائف التبريد. في هذه العملية، يتم تبريد الهواء إلى 13 C. كما تتكثف الرطوبة على لفائف، فإنه يطلق حرارته الكامنة وهذه الحرارة يجب إزالتها من قبل سائل التبريد. في الشكل 9 إزالة الرطوبة A→B، هو حوالي ثلث المطلوبة لتبريد الهواء، B→C..
يظهر مخطط نموذجي في الشكل 10. يبدو المخطط معقدا ، ولكنك تعرف الأفكار الأساسية البسيطة:
* الهواء الداخلي هو مزيج من الهواء الجاف وبخار الماء.
* هناك كمية محددة من إجمالي الطاقة، وتسمى enthalpy، في الخليط عند درجة حرارة محددة، محتوى الرطوبة، والضغط.
* هناك حد أقصى لكمية بخار الماء في الخليط في أي درجة حرارة معينة.

## Slide 25
HVAC Next
Next lecture: Thermal comfort مبادئ الراحة الحرارية
Thank you very much