## Slide 1: Introduction to Power Quality
Assistant prof. Ammar Issa Ismael

## Slide 2: Introduction to Power Quality
What is power quality?
  Why it matters
  Common causes
Power quality refers to maintaining a stable voltage, current, and frequency in the power system. Poor power quality can damage equipment, reduce efficiency, and cause unexpected shutdowns. Voltage disturbances like sags and swells are caused by switching, faults, or lightning.
Diagram: Power quality impact on waveform

## Slide 3: What is Power Factor?
Definition: PF = P / S
  Impact of poor PF
  Mathematical relation
Power factor is a measure of how effectively electrical power is converted into useful work output. It is the cosine of the phase angle between voltage and current. Low power factor causes increased losses and penalties from utilities.
Power Triangle from Rashid's Book

## Slide 4: Reactive Power in the System
Difference between real and reactive power
  Inductive and capacitive loads
  Power triangle
Real power (P) performs useful work, while reactive power (Q) supports voltage levels. Inductive loads (motors) consume Q, while capacitors supply Q. Managing reactive power is essential for voltage stability and efficient system operation.
Real vs Reactive Power Illustration

## Slide 5: Flexible AC Transmission System (FACTS)
Improves control and power transfer
  FACTS types
  Role of SVC
FACTS devices enhance transmission capability and dynamic stability using power electronics. They can be series, shunt, or a combination. SVC is a shunt-type device used for voltage regulation by managing reactive power.

## Slide 6: Static VAR Compensator (SVC)
Definition and function
  Where used
  How it responds
SVC controls voltage by absorbing or injecting reactive power. It is widely used in substations and industries to prevent voltage sags and swells. It reacts dynamically to system voltage changes in real time.
Block Diagram: SVC with TCR & TSC

## Slide 7: SVC Configuration: TCR and TSC
TCR = controlled reactor
  TSC = switched capacitor
  Combined operation
TCR provides variable inductive compensation using thyristors and reactors. TSC offers step-wise capacitive compensation by switching capacitors in and out. Together they maintain voltage by adjusting reactive power dynamically.
Schematic: TCR operation with firing angle control

## Slide 8: Thyristor Controlled Reactor (TCR)
Absorbs reactive power
  Firing angle control
  Impedance variation
TCR uses thyristors to vary the conduction period in each AC cycle, thus changing the effective reactance. The firing angle (α) determines how much current flows through the reactor and how much reactive power is absorbed.
Diagram: TSC ON/OFF control logic

## Slide 9: Thyristor Switched Capacitor (TSC)
Injects reactive power
  Operates in steps
  No continuous control
TSC switches capacitors ON/OFF using thyristors without phase-angle control. During voltage sag, it injects reactive power to support voltage. It provides fast and step-changed compensation.
Feedback Control Loop in SVC

## Slide 10: SVC Control Strategy
Voltage feedback
  Dynamic response
  Control actions
SVC uses a feedback loop comparing actual voltage to a reference. Based on this, it decides to activate TCR or TSC. The control ensures system voltage stays within acceptable limits during load or fault conditions.
Voltage sag/swell waveform example

## Slide 11: Voltage Sag and Swell
Sag: 0.1–0.9 pu
  Swell: >1.1 pu
  Causes and effects
Voltage sags and swells are temporary deviations from nominal voltage. Sags are caused by faults or large loads starting, while swells may occur due to load shedding. These can damage sensitive equipment if not mitigated.

## Slide 12: MATLAB Simulink Model
SVC Model Components
  Power source, load, TCR, and TSC
  Used for performance analysis
A Simulink model replicates real-time behavior of the power system including source, load, and SVC. It helps visualize voltage changes and validate control strategies under sag/swell conditions.

## Slide 13: Waveforms Without SVC
Uncompensated voltage
sag and swell
  Higher Total Harmonic
  Distortion
  Instability observed
Without SVC, voltage sag drops the system voltage below acceptable limits and swells may exceed equipment ratings. This causes loss of equipment lifespan and malfunction. THD increases significantly.
Waveform: Stabilized voltage with SVC

## Slide 14: Waveforms With SVC
Stable voltage levels
  Reduced distortion
  Corrective action via TSC and TCR
With SVC active, sag is corrected by TSC switching ON to inject reactive power, and swell is mitigated by TCR absorbing excess reactive power. The result is a more stable voltage and improved power factor.

## Slide 15: Firing Angle Impact on TCR
Controls amount of reactive
power absorbed
  α = 90° → No conduction
  α < 90° → Increased
  conduction
Reactive current depends on firing angle α: I(α) = (Vm / XL) * [1 - (2α/π) - (sin(2α)/π)] This equation shows that by adjusting α, we can control how much inductive power is absorbed.
TSC switching diagram (stepwise)

## Slide 16: Example: Power Factor Correction
Given: 10 kW load at 0.7
lagging PF
  Target PF: 0.95
  Find required capacitor size
S = 10 / 0.7 = 14.29 kVA Q_initial = √(S² - P²) ≈ 10.2 kVAR Q_required = 10 * (tan cos⁻¹(0.7) - tan cos⁻¹(0.95)) ≈ 6.56 kVAR Capacitor of 6.56 kVAR needed to correct PF to 0.95.
Transmission System with SVC connection

## Slide 17: Example: Power Factor Improvement with SVC
Power Factor Improvement Example: Before and After Adding SVC
🧮 Given:
A 3-phase load consumes:
  Active Power P=100 kW
  Operating at power factor cos⁡(ϕ1)=0.7 lagging
  Line Voltage: V=400 V (rms)
  Frequency: f=50 Hz
We aim to improve the power factor to cos⁡(ϕ2)=0.95 using an SVC
Step 1: Before SVC — Calculate Reactive Power

## Slide 18: Example: Power Factor Improvement with SVC
🔺 Step 2: After SVC — Target Power Factor (0.95)
⚖️ Step 3: Reactive Power Compensation Required
So, the SVC must supply 69.18 kVAR of leading reactive power to improve the power factor from 0.7 to 0.95.
📦 Capacitor Bank Sizing (TSC):
For a three-phase system

## Slide 19: Example: Power Factor Improvement with SVC

## Slide 20: Applications of SVC
Used in transmission and distribution
  Industrial loads like motors
  Renewables like wind/solar
SVC ensures voltage quality in high-power applications, supports integration of renewables, and improves the power factor of inductive industrial loads.

## Slide 21: Limitations and Considerations
Thyristor switching causes harmonics
  High capital cost
  Requires advanced control systems
Although effective, SVC introduces harmonics due to thyristor switching and requires proper filtering. Economic feasibility must be evaluated for small-scale use cases.

## Slide 22: Conclusion
SVC = TCR + TSC
  Improves PF and voltage stability
  Essential for modern grids
Static VAR Compensators offer dynamic voltage control and reactive power management. Their modular design and quick response make them ideal for grid support.